ATTACHMENT 1

FURNISHING PARKING LOT PAVING AND STRIPING AT KAUMUALII STATE PARK, WAILUA, KAUAI, HAWAII, DEPARTMENT OF LAND AND NATURAL RESOURCES, DIVISION OF STATE PARKS

SPECIAL PROVISIONS

A.  SCOPE OF WORK

Contractor shall furnish all labor, equipment, tools, materials and transportation/mobilization to perform all operations in connections with providing parking lot paving and striping services at the Kaumualii State Park, Wailua, Kauai, Hawaii.

The Department of Land and Natural Resources (DLNR) Division of State Parks will require the contractor to :

1.  Install and maintain Best Management Practices (BMP’s)

2.  Cold planing existing A.C. pavement 2” deep , starting from the end of the existing paved driveway, 1,900 SY.  To include the existing ADA parking and loading area

3.  Install new aggregate base course, 2” thick, 1,900 SY

4.  Level, grade and compact existing gravel and base course for drainage so that there is no ponding on the new pavement, 1,900 SY

5.  A.C. paving State Mix V, 1,900 SY

6.  Repaint ADA and loading area markings, install new cement wheelstop

7.  Remove and replace 40’ of 1” schedule 80 PVC domestic water pipe .  New PVC pipe to include a 1.5”schedule 80 PVC chase pipe covering the 1” pipe

8.  Remove and properly dispose of any excess excavated/cold planing materials, gravel, and dirt from the job site.

9.  Identify domestic water meter.  Identify electric box on driveway shoulder.

10.  Ok to move rocks in preparation for cold planing, grading, and AC paving.  Rocks to be placed back in exact locations prior to paving.

11.   Ok to barricade and close the job site during non work hours as not to damage any prep work taking place.

CONTRACT ADMINISTRATOR

For the purpose of this contract, David Tsuchiya, Kauai State Parks Superintendent of the Department of Land and Natural Resources, or designee, is the designated Contract Administrator (CA).  The telephone number at which he may be reached is 808-274-3447   Cell 808-346-3921

TERM OF CONTRACT

The term of this contract shall be for a 1 time paving and ADA striping of the parts and materials listed above.  The contract shall begin once an approved purchase order has been received by the Department of Land and Natural Resources, Division of State Parks.  Contract end shall be when payment has been received by the contractor from the State of Hawaii, Division of State Parks.

OFFEROR QUALIFICATIONS

Offeror must be (HCE) Hawaii Compliance Express certified.  Offeror must also have a permanent office location in Hawaii where he/she will be accessible to telephone calls regarding complaints or requests that need immediate attention.  Offeror shall have adequate equipment and number of employees to perform and complete the work specified herein within the period specified if awarded the contract.  Offeror must possess and provide a Contractor A license.

BID QUOTATION

Unit bid price shall include labor, parts, all applicable taxes and any other costs    
incurred to provide services specified above.

GENERAL

- All work must be done between 7:00 AM and 4:30 PM, Monday through Friday, except on State Holidays

- The Contractor shall provide safety signs, barricades, and other devices necessary for the safety and convenience of the general public.  The Contractor shall at all times conduct his/her work to assure the least possible disruption to normal public traffic (vehicular and pedestrian), allowing for the free flow of traffic and public right of ways.

- Any damage to plants and other property or items in the area and adjoining properties shall be repaired and/or replaced by the contractor at his/her own expense and restored to the satisfaction of the Contract Administrator and the injured party(ies).

SITE INSPECTION

Prior to submittal of an offer, offerors may inspect the location to familiarize themselves with existing conditions, rules and regulations, and the extent and nature of work to be performed.  Offeror inspection is not mandatory, however, submission of an offer shall be evidence that the offeror understands the scope of the project and shall comply with specifications herein, if awarded the contract.  No additional compensation, subsequent to bid opening, shall be allowed by reason of any misunderstanding or error regarding site conditions or work to be performed.

Tax Liability

Work to be performed under this solicitation is a business activity taxable under Chapter 237, HRS, and vendors are advised that they are liable for the Hawaii General Excise Tax (GET) at the current 4% rate.  If, however an Offeror is a person exempt by the HRS from paying the GET and therefore not liable for the taxes on this solicitation, Offeror shall state its tax exempt status and cite the HRS chapter or section allowing the exemption.

Award of Contract

Compliance – “Offeror is advised that in order to be awarded a contract under this  solicitation, the vendor/contractor/service provider will be required to be compliant with all laws governing entities doing business in the State including the following chapters and pursuant to HRS 103D-310©:

- Chapter 237, tax clearance;

- Chapter 383, unemployment insurance;

- Chapter 386, workers compensation;

- Chapter 392, temporary disability insurance;

- Chapter 393, prepaid health care; and

- Section 103D-310©, Certificate of Good Standing for entities doing business in the State.  The State will verify compliance on Hawaii Compliance Express for awards $2500 or greater.  The HCE is an electronic system that allows vendors/contractors/service providers doing business with the state to quickly and easily demonstrate compliance with applicable laws.  It is an online system that replaces the necessity of obtaining paper compliance certificates from the Department of Taxation; Federal Internal Revenue Service; Department of Labor and Industrial Relations; and Department of Commerce and Consumer Affairs.  Vendors/contractors/service providers should register with (HCE) prior to submitting an offer at https://vendors.ehawaii.gov.  The annual registration fee is $12.00 and the Certificate of Vendor Compliance is accepted for both contracting and final payment.

## LIABILITY INSURANCE

The Contractor shall maintain in full force and effect during the life of this contract, liability and property damage insurance to protect the Contractor and his subcontractors, if any, from claims for damages for personal injury, accidental death and property damage which may arise from operations under this contract, whether such operations be by himself or by a subcontractor or anyone directly or indirectly employed by either of them. If any subcontractor is involved in the performance of the contract, the insurance policy or policies shall name the subcontractor as additional insured.

As an alternative to the Contractor providing insurance to cover operations performed by a subcontractor and naming the subcontractor as additional insured, Contractor may require subcontractor to provide its own insurance which meets the requirements herein. It is understood that a subcontractor's insurance policy or policies are in addition  to the Contractor's own policy or policies.

The following minimum insurance coverage(s) and limit(s) shall be provided by the Contractor, including its subcontractor(s) where appropriate.

## Coverage	Limits

Commercial General Liability	$1,000,000 combined single limit per occurrence for bodily injury and property damage

$2,000,0000 general aggregate

Automobile Liability	$1,000,000 combined single limit per occurrence

$1,000,000 bodily injury per person and per accident

$1,000,000 property damage per accident

Each insurance policy required by this contract, including a subcontractor's policy, shall contain the following clauses:

1.	Chapter 383, unemployment insurance;

2.	Chapter 386, workers’ compensation;

3.	Chapter 392, temporary disability insurance;

4.	Chapter 393, prepaid health care; and

5.	Section 103D-310(c), Certificate of Good Standing (COGS) for entities doing business in the State.

The State will verify compliance on Hawaii Compliance Express (HCE) for awards

$2,500 or greater. The HCE is an electronic system that allows vendors/contractors/ services providers doing business with the state to quickly and easily demonstrate compliance with applicable laws. It is an online system that replaces the necessity of obtaining paper compliance certificates from the Department of Taxation; Federal Internal Revenue Service; Department of Labor and Industrial Relations; and Department of Commerce and Consumer Affairs.

Vendors/contractors/service providers should register with (HCE) prior to submitting an offer at https://vendors.ehawaii.gov. The annual registration fee is $12.00 and the ‘Certificate of Vendor Compliance’ is accepted for both contracting and final payment.”

- "This insurance shall not be canceled, limited in scope of coverage or non-renewed until after 30 days written notice has been given to the State of Hawaii, Department of Land and Natural Resources, Division of State Parks, P. O. Box 621, Honolulu HI 96809.”

- "The State of Hawaii is added as an additional insured as respects to operations performed for the State of Hawaii

- “It is agreed that any insurance maintained by the State Of Hawaii will apply in excess of, and  not contribute with, insurance provided by this  policy

The minimum insurance required shall be in full compliance with the Hawaii Insurance Code throughout the entire term of the contract, including supplemental agreements.

Upon Contractor's execution of the contract, the Contractor agrees to deposit with the State of Hawaii certificate(s) of insurance necessary to satisfy the State that the insurance provisions of this contract have been complied with and to keep such insurance in effect and the certificate(s) therefore on deposit with the State during the entire term of   this contract, including those of its subcontractor(s), where appropriate. Upon request by the State, Contractor shall be responsible for furnishing a copy of the policy or policies.

Failure of the Contractor to provide and keep in force such insurance shall be regarded as material default under this contract, entitling the State to exercise any or all of the remedies provided in this contract for a default of the Contractor.

The procuring of such required insurance shall not be construed to limit Contractor's liability hereunder nor to fulfill the indemnification provisions and requirements of this contract. Notwithstanding said policy or policies of insurance, Contractor shall be obliged for the full and total amount of any damage, injury, or loss caused by negligence or neglect connected with this contract.

## START OF WORK

Work will commence within ten (10) calendar days of the date of the notice to proceed issued by the Department of Land and Natural Resources. The Contractor must notify the Contract Administrator in advance before starting work at any location. The Contract Administrator shall schedule the priority of work.

## INVOICING

Contractor shall send an original and three (3) copies of the invoice upon completion of all services listed in the purchase order. The original shall state that “This is an original bill”, shall be signed and sent to:

Department of Land and Natural Resources Division of State Parks

3060 Eiwa St .Room 306

Lihue, Hi 96766

Invoice should reference the purchase order number.

A tax clearance certificate, not over two months old, with an original green certified copy stamp, must accompany the invoice for final payment on the contract.

## SUBCONTRACTORS

The Contractor shall not delegate any duties unless the Contract Administrator has given written approval. The State reserves the right to approve all subcontractors and shall require the primary contractor to replace any subcontractors found to be unacceptable. The primary contractor will be the sole point of contact with regard to contractual matters, including payment of any and all charges resulting from the contract, and shall be responsible for all services whether or not the primary contractor performs them.

## WORKMANSHIP

All work shall be executed in a workmanlike manner, and shall present a neat appearance when completed. Services rendered shall follow the Scope of Work and these Special Provisions, subject to inspection and approval of the Contract Administrator.

## RE-EXECUTION OF WORK

The Contractor shall re-execute any work that fails to conform to the requirements of the contract and shall immediately remedy any defects due to faulty workmanship    by the Contractor. Should the Contractor fail to comply, the State reserves the right to engage the services of another company to perform the services and to deduct such costs from monies due to the Contractor.