STATE OF HAWAII

DEPARTMENT OF HEATLH

ADULT MENTAL HEALTH DIVISION

HAWAII STATE HOSPITAL

45-710 KEA'AHALA ROAD

KANEOHE, HI 96744

HIePRO SOLICITATION

REQUEST FOR QUOTES: RFQ-24-06-HSH

FOR

SERVICING OF AUTOMATIC TRANSFER SWITCHES AT BOTH UPPER & LOWER CAMPUS OF HAWAII STATE HOSPITAL

Release: July 26, 2023

Offer Due:  August 9, 2023, 2:00 PM (HST)

Hawaii State Hospital (HSH) is seeking a contract for the servicing & maintenance of the Automatic Transfer Switches at both the upper & lower campus on the grounds of Hawaii State Hospital set forth in Section 1, Scope of Services, of this solicitation Request for Quote (hereinafter “RFQ”).

- Scope of Services

Upper Campus:

- Verify that the transfer switch nameplate values are correct with the application (voltage, current, etc.)

- Verify that equipment ground connection is properly terminated.

- Verify that the phase rotations of both sources are matched

- Verify that any customer auxiliary contacts are properly terminated (position, pre-signal, etc.)

- If applicable, verify that any load control wiring is properly terminated (load add, shed, etc,)

- Review communications connections to an external SCADA or Building Automation System, if applicable.

- Lubricate any necessary moving linkages, bearings, etc.

- Adjust mechanical limit switches, if necessary & review with on site personnel

- Perform a second Load Test of the transfer switch

- With the transfer switch in the S2 position, open the S2 source breaker & verify immediate re-transfer to S1 position. Logistics & freight will be included.

Break down

Following equipment to be serviced:

- 1ea. 800A (ATS CUP) Zenith ATS, branded Kohler

- 1ea. 150A (ATS CUPEC) – Zenith ATS, branded Kohler

- 1ea. 2000A )NPF ATS) ASCO ATS branded Kohler

- 1ea. 1200A (Critical ATS) Zenith ATS, branded Kohler

Lower Campus

- Each vacuum breaker will be cleaned & inspected for physical damage.

- All lubricant points will be performed according to manufacturer's specifications.

- A mechanical test will be performed according to manufacturer’s specifications.

- An AC or DC high potential test will be performed on each bottle with the breaker in the open position.

- The primary contact resistance of each phase will be measured with a ductor and data recorded.

- After cleaning a phase to phase and phase to ground insulation resistance test will be performing using a 1000 volt megohmmeter.

- The test data obtained will be included as part of the Engineering Report.

Breakdown

Following equipment to be serviced:

- 4 Generator Switchgear Medium Voltage Vacuum Circuit Breakers, VR-15050-12

- 1200A, 15KV, Emergency Generator, Square D Medium Voltage CB

- 1200A, 15KV, Loadbank, Square D Medium Voltage CB

- 1200A, 15KV, Main, Square D Medium Voltage CB

- 1200A 15 KV, Pad Mounted Switch 1, Square D Medium Voltage CB

- 8 Main Switchgear Medium Voltage Vacuum Circuit Breakers, 150VCP-W500

- 1200A, 15KV, Utility Incoming 1, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, Utility Incoming 2, Cutler Hammer Medium Voltage CB

- 1200A,  15KV, Switchgear Main CB, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, 50 KVA Xfmr, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, Loop Feeder Lower, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, Spare, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, Loop Feeder Upper, Cutler Hammer Medium Voltage CB

- 1200A, 15KV, Standby Generator, Cutler Hammer Medium Voltage CB

|  | General Description |
| --- | --- |
| Prebid Conference | All Contractors must attend a mandatory meeting at the Hawaii State Hospital on August 2, 2023, at 0900. To do a walk through to evaluate scope of work. Call/email Facility Plant Manager to confirm interest/attendance. |
| Completion of Work | At completion of the work, Contractor will provide a written warranty that the completed project is free from any workmanship or material defects for a period of one (1) year starting from the date of the works formal acceptance. The warranty shall state that, in case of any workmanship defects that will occur within the period of one (1) year, the Contractor shall implement the necessary corrective work without charging the State for the costs of materials, labor, and equipment use. |
| Professional Reference | Provide 3 References for Hawaii State Hospital to contact. - Reference #1 - Reference #2 - Reference #3 |

General Compliance     General guideline to follow while on HSH Property

      - All work shall be done between 7:30am to 3:00pm, Monday through Friday, except State Holidays.

      - The duration of this work shall be no longer than ninety (90) work days, excluding rain out days unless agreed to be Hawaii State Hospital Facility Plant Manager.

      - Contractor to provide safety signs, barricades, and other devices necessary for the safety and convenience of the general public. Contractor shall at all times conduct his/her work to assure the least possible disruption to normal public traffic (vehicular and pedestrian) and allowing for the free flow of traffic and public rights-of way.

      - Shirts are required to be worn at all times on the work site, smoking is not allowed anywhere on the property, no radios or headsets are allowed.

      - Adverse conditions which may require major field changes not stated in the scope of work for this project must be reported to the Hawaii State Hospital Facility Plant Manager prior to commencement or continuation of work.

      - Contractor shall re-execute any work that fails to conform to the requirements of this agreement and shall immediately remedy any defects due to faulty workmanship by the Contractor. Should the Contractor fail to comply, the State reserves the right to engage the services of another company to perform the services and to deduct such costs from monies due to the Contractor.

- Qualification and Requirement:

- Prevailing wages will apply

- Provide qualified candidates to perform the services under this RFQ.

- Maintain an accurate record and shall report to HSH Facility Plant Manager.

- Certificate of insurance.

- Vendor Compliance

- Proof of compliance obtained through Hawaii Compliance Express (HCE). The vendor’s name on the Certificate of Vendor Compliance (CVC) must exactly match the vendor’s name under which the quote for this solicitation is submitted. A copy of CVC must be submitted with quote for verification. The vendor is responsible for maintaining compliance. Non-compliance may result in a vendor not receiving an award, delay of payment, or cancellation of award.

- The interested offeror must be a registered company to do business in the State of Hawaii.

- Compensation and Payment Schedule

The Contractor shall be compensated in accordance with the Rate Schedule that are offered and submitted by the Contractor in responding to this RFQ (See Rate Schedule attached herein).

The Contractor shall submit monthly invoice to Hawaii State Hospital for the services provided in accordance with Section 1, “Scope of Services.”

- Performance Period:

The Contractor shall provide the services required under the contract from August 10, 2023, to June 30, 2024 unless the contract is sooner terminated.

When in the interest of the State, HSH may terminate the contract at any time and for convenience by providing eight (8) weeks prior written notice to the Contractor.

- Submission and Award

The compensation rates in the Rate Schedule that are offered by the Contractor shall be inclusive of wages, fringe benefits, all applicable taxes, and all incidental costs (if any).

All submittals shall be made via HIePRO. The following documents must also be completed and submitted by the vendor.

- Form W-9

- Wage Certificate

- Offeror’s Qualification Form

- Offer Form OF-1

- Rate Schedule (see Rate Schedule attached herein)

Selection and award shall be contingent on the lowest and most responsible and responsive offer.

HSH reserves the right to cancel this procurement or award at any time and for convenience by providing eight (8) weeks prior written notice to the Contractor.

Please contact Troy Adams at (808) 306-0431 or troy.adams@doh.hawaii.gov if you have any questions regarding this RFQ.