YSTATE OF HAWAII

DEPARTMENT OF HEATLH

ADULT MENTAL HEALTH DIVISION

HAWAII STATE HOSPITAL

45-710 KEA'AHALA ROAD

KANEOHE, HI 96744

HIePRO SOLICITATION

REQUEST FOR QUOTES: RFQ-HSH-24-630-008

FOR

REPAIR OF (3) FAN BLOWER ASSEMBLY UNITS

Release: August 2, 2023

Offer Due:  August 16, 2023, 2:00 PM (HST)

Hawaii State Hospital (HSH) is seeking a contract for the repair of air handling units at buildings F,H &I on the grounds of Hawaii State Hospital set forth in Section 1, Scope of Services, of this solicitation Request for Quote (hereinafter “RFQ”).

- Scope of Services

Repair Work

- Remove & dispose of equipment from York XTI AHU for buildings: F, H & I.

- Deliver & install one new fan assembly with new motor & any other parts necessary to return the air handler to normal service in each building.

- Installation work must be scheduled with Plant Ops.

- Adjust fan belts & align sheaves & any other work required for the new fan wheel assembly & motor to run properly.

- Start up & test to insure proper functioning.

- At completion of the work, Contractor will provide a written warranty that the completed project is free from any workmanship or material defects for a period of 1 year starting from the date of the works formal acceptance. The warranty shall state that, in case of any workmanship defects that will occur within the 1 year, the Contractor shall implement the necessary corrective work without charging the government for the costs of materials, labor & equipment use.

Equipment:

Bldg F: XTI-054X078-BAJA046A

Bldg H: XTI-045XO75-BAHA046A

Bldg I:   XTI-054X078-FAHA046A

|  | General Description |
| --- | --- |
| Prebid Conference | All Contractors must attend a mandatory meeting at the Hawaii State Hospital on August 30, 2023 at 09:00. To do a walk through to evaluate scope of work. Call/email Facility Plant Manager to confirm interest/attendance. |
| Completion of Work | At completion of the work, Contractor will provide a written warranty that the completed project is free from any workmanship or material defects for a period of one (1) year starting from the date of the works formal acceptance. The warranty shall state that, in case of any workmanship defects that will occur within the period of one (1) year, the Contractor shall implement the necessary corrective work without charging the State for the costs of materials, labor, and equipment use. |
| Professional Reference | Provide 3 References for Hawaii State Hospital to contact. - Reference #1 - Reference #2 - Reference #3 |

General Compliance     General guideline to follow while on HSH Property

      - All work shall be done between 7:30am to 3:00pm, Monday through Friday, except State Holidays.

      - The duration of this work shall be no longer than ninety (90) workdays, excluding rain out days unless agreed to be Hawaii State Hospital Facility Plant Manager.

      - Contractor to provide safety signs, barricades, and other devices necessary for the safety and convenience of the general public. Contractor shall at all times conduct his/her work to assure the least possible disruption to normal public traffic (vehicular and pedestrian) and allowing for the free flow of traffic and public rights-of way.

      - Shirts are required to be worn at all times on the work site, smoking is not allowed anywhere on the property, no radios or headsets are allowed.

      - Adverse conditions which may require major field changes not stated in the scope of work for this project must be reported to the Hawaii State Hospital Facility Plant Manager prior to commencement or continuation of work.

      - Contractor shall re-execute any work that fails to conform to the requirements of this agreement and shall immediately remedy any defects due to faulty workmanship by the Contractor. Should the Contractor fail to comply, the State reserves the right to engage the services of another company to perform the services and to deduct such costs from monies due to the Contractor.

- Qualification and Requirement:

- Prevailing wages will apply.

- Provide qualified candidates to perform the services under this RFQ.

- Maintain an accurate record and shall report to HSH Facility Plant Manager.

- Certificate of insurance.

- Vendor Compliance

- Proof of compliance obtained through Hawaii Compliance Express (HCE). The vendor’s name on the Certificate of Vendor Compliance (CVC) must exactly match the vendor’s name under which the quote for this solicitation is submitted. A copy of CVC must be submitted with quote for verification. The vendor is responsible for maintaining compliance. Non-compliance may result in a vendor not receiving an award, delay of payment, or cancellation of award.

- The interested offeror must be a registered company to do business in the State of Hawaii.

- Compensation and Payment Schedule

The Contractor shall be compensated in accordance with the Rate Schedule that are offered and submitted by the Contractor in responding to this RFQ (See Rate Schedule attached herein).

The Contractor shall submit monthly invoice to Hawaii State Hospital for the services provided in accordance with Section 1, “Scope of Services.”

- Performance Period:

The Contractor shall provide the services required under the contract from August 17, 2023, to August 16, 2024, unless the contract is sooner terminated.

When in the interest of the State, HSH may terminate the contract at any time and for convenience by providing eight (8) weeks prior written notice to the Contractor.

- Submission and Award

The compensation rates in the Rate Schedule that are offered by the Contractor shall be inclusive of wages, fringe benefits, all applicable taxes, and all incidental costs (if any).

All submittals shall be made via HIePRO. The following documents must also be completed and submitted by the vendor.

- Form W-9

- Wage Certificate

- Offeror’s Qualification Form

- Offer Form OF-1

- Rate Schedule

Selection and award shall be contingent on the lowest and most responsible and responsive offer.

HSH reserves the right to cancel this procurement or award at any time and for convenience by providing eight (8) weeks prior written notice to the Contractor.

Please contact Troy Adams at (808) 306-0431 or troy.adams@doh.hawaii.gov if you have any questions regarding this RFQ.