Fire protection requirements for remodeled lab space

- Install an automatic sprinkler system per IBC Section 903.2.11.6  requiring sprinkler protection for all buildings containing laboratory suites.

  - Provide a water supply for the sprinkler system per NFPA 13 section 5.1.1 and 5.1.2.   The water supply must be reliable and readily available.  All sprinkler systems with more than 20 sprinkler heads must be monitored by an authorized 24-hour monitoring agency.

  - Provide a fire pump that delivers the water supply to the sprinkler system at the flow rate and pressure required by NFPA 13.  The fire pump can be typically powered by a diesel engine or an electric motor.

  - Provide added water for use as a hose-stream in addition to what is required for the sprinkler system per NFPA 13 section 19.2.6.2

- Fire apparatus access roads.   Approved fire apparatus access roads must be provided for all new facilities Per IBC Section 503.1.1.

- Install fire hydrant systems.  All new buildings must be within 400 ft. of a fire hydrant per IBC Section 507.5.1.