STATE OF HAWAII

# NATURAL ENERGY LABORATORY OF HAWAII AUTHORITY

NELHA Variable Frequency Drive Procurement

HIePRO Solicitation: 26001734

eIFB-26-04-NELHA

Solicitation Description: The general Scope of Services for this solicitation will be to procure a 240 A (line item #1) variable frequency drive (VFD) and a 124 A (line item #2) VFD. The VFD require integration with the control parameters in NELHA’s existing ABB ACH550-UH-240-4, ABB ACQ580-01-240A-4, ABB ACH550-UH-125-4, and ABB ACQ580-01-124A-4 drives. The control parameters will include:

- Take lead or follow roles in the PID controls.

- Startup stand by pumps if primary lead or lag pump faults or system demand requires additional pumps.

- Shut down lag pumps when the system demand does not require additional helper pumps.

The VFD manufacturer shall demonstrate they can integrate seamlessly with current ABB ACH 550-UH and ABB ACQ580-01 drives in the NELHA pump control system.

In addition to the control parameters integration, the VFD will require hot swappability with our existing ABB ACH550-UH-240-4, ABB ACQ580-01-240A-4, ABB ACH550-UH-125-4, and ABB ACQ580-01-124A-4 drives. NELHA runs a 24/7/365 seawater pumping utility that live animals rely on the constant water circulation. The system cannot be down for more than 2 hours. The VFD will require the motor leads attachment points, communication connections and bolt mountings to be located in similar locations as our current ABB VFD Drives. The VFD manufactures shall demonstrate that conductors, and communication connections  will not be required to be re-routed or re-pulled due to length issues in order to hot swap a non-working VFD with a working VFD. Wall mounting holes will need to be in similar locations to avoid any drilling to hot swap a non-working VFD with a working VFD.

All line-item pricing shall include all related procurement costs, including shipping and handling costs to the NELHA facility in Kailua Kona, Hawaii.

| Item | Title | Description | Commodity Code | Description | UoM | Qty |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 240 A VFD | ABB ACQ580-01-240A-4-BO56+C218+K491 ( 240 A Variable Frequency Drive for a 200 hp Pump) or Equivalent Specification VFD |  |  | EACH | 2 |
| 2 | 124 A VFD | ABB ACQ580-01-124A-4-B056+C218+K491 (124 A Variable Frequency Drive for a 100 hp Pump) or Equivalent Specification VFD |  |  | EACH | 8 |

LINE ITEM 1 SPECIFICATIONS: ABB ACQ580-01-240A-4-BO56+C218+K491

- Nominal Horsepower: 200

- Input Voltage Rating: 480 VAC 3-Phase (+/- 30%)

- Input Frequency: 48-63 Hz

- Input Line Limitations: Max +/13% of nominal phase to phase Input voltage

- Input Fundamental Power Factor: 0.98 at nominal load

- Rated Output Current: 240 Amps

- Output (Motor) Continuous Current: 1.0 * 12N (Nominal rated output current)

- Output Base Motor Frequency Range: 10 – 500 Hz

- Output Switching Frequency: 1, 4, 8, 12, kHz

- Output Short Circuit Withstand Rating: 100,000 AIC (UL) w/o fuses

- Agency Approval / Listing & Compliance: UL, cUL, CE

- Ambient Conditions:

  - Air Temperature: 15°C – 40°C

  - Relative Humidity: 5-95% (no condensation allowed)

  - Vibration: Max 3.0 mm – 2.9Hz, Max 10 m/s2 90-200 Hz

- Analog Input: Two (2) programmable analog inputs

- Analog Output: Two (2) programmable analog outputs

- Digital Inputs: Six (6) programmable digital inputs

- Internal Power Supply: +24 VDC max 250 mA (short circuit protection)

- Relay Outputs: Three (3) programmable relay outputs +24 VDC or 250 VAC, 0.4 A at 120 VDC

- Protections:

  - Single Phase: Protected (input & output)

  - Overcurrent Trip Limit: 3.5 x 12N instantaneous

  - Adjustable Current Regulation Limit: 1.1 x l2N(RMA) max

  - Under Voltage Trip Limit: 1.30 x Un

  - Over Temperature (Heatsink): + 115°C (+239°F)

  - Auxiliary Voltage: Short Circuit Protected

  - Ground Fault: Protected

  - Short Circuit: Protected

  - Microprocessor Fault: Protected

  - Motor Stall Protection: Protected

  - Motor Over Temperature Protection: Protected

  - Input Power Loss of Phase: Protected

  - Loss of Reference: Protected

  - Short Circuit Current Rating: 100,000 RMS symmetrical Amperes

  - Input Line Impedance: 5% equivalent

- Enclosure: UL (NEMA) Type 12 (OPTION +B056)

- Frame Size: R8

- Input Impedance: 5%

- Short Circuit Current Rating: 100kA with fuse

- Communication Protocols: Modbus RTU, Modbus/ TCP adapter (OPTION +K491)

- Other Options: Conformally Coated Drive PCBs to Comply class 3c4 (IEC60721-3-3:2002) (+C218)

- Fuse Class: JJS-350

- Max Amps (600V): 350

- Input Wiring: 2*1/0 AWG (2*50 mm^2) (29.5 ft-lb or 40 Nm)

- Output Wiring: 2*1/0 AWG (2*50 mm^2) (29.5 ft-lb or 40 Nm)

- Ground Wiring: 2*350 MCM (2x185 mm^2) (7.2 ft-lb or 9.8 Nm)

- Dimension and Weight: height 44.22" X width 13.82" X depth 17.8" / weight 170 lbs.

- Heat Dissipation: 11383 BTU/hr (3336 Watts)

- Airflow Requirements: 324 CFM (550 CM/hr)

- Vertical Mounting Standalone: Above: 6.2” Below: 11.9” Sides 6”

- Vertical Mounting Side by Side: Above: 7.9” Below: 11.9” Sides 0”

- VFD keypad with built in time clock with battery backup with 10-year life span for time and date fault recording along with multiple operation functions.

- The VFD cooling fan shall turn off when not needed to increase fan life and be designed for removal without disconnecting any wiring both power or control.

- All VFD' s shall have the same customer interface regardless of horsepower rating.

- The VFD keypad shall be backlit and removable to allow uploading and downloading parameter settings.

- The VFD shall be able to communicate via Ethernet without the use of a third-party gateway.

- The keypad shall include hand-off-auto selections with bump less transfer between hand and auto.

- Internal PID functionality shall be supplied with the VFD for closed loop control.

- The VFD shall be able to be programmed via laptop. All interconnecting communications cable, modems, and/or adapters shall be supplied along with a licensed copy of the software.

- Data Display:

  - Output Frequency

  - Motor Current

  - Calculated % Motor Torque Calculated Motor Power (kW) DC Bus Voltage

  - Output Voltage

  - Heatsink Temperature

  - Elapsed Time Meter (reset-able)

  - KWh (resettable)

  - Input / Output Terminal Monitor

  - PID Actual Value (Feedback) & Error Fault Text

  - Warning Text

  - Three (3) Scalable Process Variable Displays

  - User Definable Engineering Units

- Two (2) Programmable Analog Inputs

- Six (6) Programmable Digital Inputs

- Two (2) Programmable Analog Outputs

- Up to Six (6) Programmable Relay Outputs (Three (3) Standard)

- Input Speed Signals”

  - Current O (4) to 20 mA

  - Voltage O (2) to 10 VDC

  - Increase/Decrease Reference Contacts (Floating Point)

  - Serial Communications

- Input Speed Signals:

  - Current O ( 4) to 20 mA

  - Voltage O (2) to 10 VDC

  - Increase/Decrease Reference Contacts (Floating Point)

  - Serial Communications

- Start/Stop:

  - 2 Wire (Dry Contact Closure)

  - 3 Wire (Momentary Contact)

  - Application of Input Power

  - Application of Reference Signal (PID Sleep/Wake-Up)

  - Serial Communications

- Start Functions:

  - Ramp

    - Flying Start

    - Pre-Magnetization (DC Brake) on Start

  - Automatic Torque Boost

  - Automatic Torque Boost with Flying Start

  - Auto Restart (Reset) - Customer Selectable and Adjustable

- Stop Functions:

  - Ramp or Coast Stop

  - Emergency Stop

  - DC Braking / Hold at Stop

  - Flux Braking

- Timer Functions:

  - Four (4) Daily Start/Stop Time Periods

  - Four (4) Weekly Start/Stop Time Periods

  - Four Timers for Collecting Time Periods and Overrides

- Supervision Functions

- Adjustable Current Limit

- Automatic Extended Power Loss Ride Through (Selectable)

- PID Control:

  - Two (2) Integral Independent Programmable PID Setpoint Controllers (Process & External)

  - External Selection between Two (2) Sets of Process PID Controller Parameters

  - PID Sleep/Wake Up

- Motor Control Features:

  - Scalar (V/Hz) and Vector Modes of Motor Control

  - V/Hz Shapes

  - Linear

  - Squared

  - Energy Optimization

  - IR Compensation

  - Slip Compensation

  - Three (3) Critical Frequency Lockout Bands

- Pre-programmable Protection Circuits:

  - Overcurrent

  - Short Circuit

  - Ground Fault

  - Over Voltage

  - Under Voltage

    - Input Phase Loss

  - Output Device (IGBT) Over Temperature

  - Adjustable Current Limit Regulator

  - UL508C approved Electronic Motor Overload (I2T)

- Programmable Fault Functions for Protection Include:

  - Loss of Analog Input

  - Panel Loss

  - External Fault

  - Motor Thermal Protection

  - Stall

  - Under load

  - Motor Phase Loss

  - Ground Fault

- Input Impedance

  - 5% Equivalent Impedance with Internal Reactors(s)

- Include Ethernet Card

  - Modbus/TCP adapter ( one port) shall be included with the specified VFD.

General Specification Requirements:

- Any changes to these features, specifications and requirements shall be put in writing by the vendor and approved by the NELHA Officer-in-Charge (OIC). For the sake of this solicitation and installation of the equipment, the NELHA OIC will be Keith Olson, Chief Operations and Science Officer or his designated representative.

- Manufacturer/Vendor shall provide on-site or on-line (Zoom or Teams) start up assistance by a factory authorized and trained technician.

- Warranty: 2 year on site parts and labor from date of shipment with NELHA Technicians performing the install and start up.

- The VFD shall be ABB ACQ580 Series VFD for Water Pumping Application, Drive Only; model ABB ACQ580-01-240A-4 or Equal VFD in strict accordance with the above features, specifications, and services.

Communication and Control Requirements:

- New VFD will be required to communicate with, take a lead or following roles in the PID controls with client's current ABB drives. VFD manufacturer shall demonstrate that they can integrate seamlessly with client's current inventory of ABB, ACH 550-UH drives when in PID lead or following roles.

- The VFD should include a Pump and Fan Alteration (PFA) mode of operation. The PFA function should contain the following major features:

  - The VFD controls the motor of pump no. 1, varying the motor speed to control the pump capacity. This motor is the speed regulated motor.

  - Direct line connections power the motor of pump no. 2 and pump no.3, etc. The ACI-1550 switches pump no. 2 (and then pump no. 3, etc.) on and off as needed. These motors are auxiliary motors.

  - The VFD PID control uses two signals: a process reference and an actual value feedback. r

  - The PID controller adjusts the speed (frequency) of the first pump such that the actual value follows the process reference.

    - When demand (defined by the process reference) exceeds the first motor's capacity ( user defined as a frequency limit), the PFA control automatically starts an auxiliary pump. The PFA also reduces the speed of the first pump to account for the auxiliary pump's addition to total output. Then, as before, the PID controller adjusts the speed (frequency) of the first pump such that the actual value follows the process reference. If demand continues to increase, PFA adds additional auxiliary pumps, using the same process.

  - When demand drops, such that the first pump speed falls below a minimum limit, the PFA control automatically stops an auxiliary pump. The PFA also increases the speed of the first pump to account for the auxiliary pump’s missing output.

  - An Interlock function (when enabled) identifies off-line (out of service) motors, and the PFA control skips to the next available motor in the sequence.

  - An Auto-change function (when enabled and with the appropriate switchgear) equalizes duty time between the pump motors. Auto-change periodically increments the position of each motor in the rotation - the speed regulated motor becomes the last auxiliary motor, the first auxiliary motor becomes the speed regulated motor, etc.

  - The VFD's programmable relays are capable of interfacing with the PFA function.

- Variable Frequency Drive Modbus Register must contain the following:

  - A Control Word capable of receiving and writing a 16-bit Word from NELHA's current SCADA system for Command/Control purposes.

  - A Reference 1 parameter capable of receiving and writing data from NELHA's current SCADA system with a range of 0 to 20000 for speed control purposes.

  - A Reference 2 parameter capable of receiving and writing data from NELHA's current SCADA system with a range of 0 to 10000 for speed control purposes.

  - A read only STATUS WORD capable writing data to NELHA's current SCADA system for the purpose of monitoring the current status of the VFD.

  - A read only FAULT WORD capable of writing data to NELHA 's current SCADA system for the purposing of monitoring active VFD faults.

LINE ITEM 2 SPECIFICATIONS: ABB ACQ580-01-124A-4-B056+C218+K491

- Nominal Horsepower: 100

- Input Voltage Rating: 480 VAC 3-Phase (+/- 30%)

- Input Frequency: 48-63 Hz

- Input Line Limitations: Max +/13% of nominal phase to phase Input voltage

- Input Fundamental Power Factor: 0.98 at nominal load

- Rated Output Current: 124 Amps

- Output (Motor) Continuous Current: 1.0 * 12N (Nominal rated output current)

- Output Base Motor Frequency Range: 10 – 500 Hz

- Output Switching Frequency: 1, 4, 8, 12, kHz

- Output Short Circuit Withstand Rating: 100,000 AIC (UL) w/o fuses

- Agency Approval / Listing & Compliance: UL, cUL, CE

- Ambient Conditions:

  - Air Temperature: 15°C – 40°C

  - Relative Humidity: 5-95% (no condensation allowed)

  - Vibration: Max 3.0 mm – 2.9Hz, Max 10 m/s2 90-200 Hz

- Analog Input: Two (2) programmable analog inputs

- Analog Output: Two (2) programmable analog outputs

- Digital Inputs: Six (6) programmable digital inputs

- Internal Power Supply: +24 VDC max 250 mA (short circuit protection)

- Relay Outputs: Three (3) programmable relay outputs +24 VDC or 250 VAC, 0.4 A at 120 VDC

- Protections:

  - Single Phase: Protected (input & output)

  - Overcurrent Trip Limit: 3.5 x 12N instantaneous

  - Adjustable Current Regulation Limit: 1.1 x l2N(RMA) max

  - Under Voltage Trip Limit: 1.30 x Un

  - Over Temperature (Heatsink): + 115°C (+239°F)

  - Auxiliary Voltage: Short Circuit Protected

  - Ground Fault: Protected

  - Short Circuit: Protected

  - Microprocessor Fault: Protected

  - Motor Stall Protection: Protected

  - Motor Over Temperature Protection: Protected

  - Input Power Loss of Phase: Protected

  - Loss of Reference: Protected

  - Short Circuit Current Rating: 100,000 RMS symmetrical Amperes

  - Input Line Impedance: 5% equivalent

- Enclosure: UL (NEMA) Type 12 (OPTION +B056)

- Frame Size: R6

- Input Impedance: 5%

- Short Circuit Current Rating: 100kA with fuse

- Communication Protocols: Modbus RTU, Modbus/ TCP adapter (OPTION +K491)

- Other Options: Conformally Coated Drive PCBs to Comply class 3c4 (IEC60721-3-3:2002) (OPTION +C218)

- Fuse Class: JJS-200

- Max Amps (600V): 200

- Input Wiring: 4 AWG (25 mm^2) (22.1 ft-lb or 30 Nm)

- Output Wiring: 4 AWG (25 mm^2) (22.1 ft-lb or 30 Nm)

- Ground Wiring: 350 MCM (185 mm^2) (7.2 ft-lb or 9.8 Nm)

- Dimension and Weight: height 34.81" X width 11.46" X depth 16.42" / weight 95 lbs.

- Heat Dissipation: 5037 BTU/hr (1476 Watts)

- Airflow Requirements: 435 CFM (256 CM/hr)

- Vertical Mounting Standalone: Above: 6.2” Below: 11.9” Sides 6”

- Vertical Mounting Side by Side: Above: 7.9” Below: 11.9” Sides 0”

- VFD keypad with built in time clock with battery backup with 10-year life span for time and date fault recording along with multiple operation functions.

- The VFD cooling fan shall turn off when not needed to increase fan life and be designed for removal without disconnecting any wiring both power or control.

- All VFD' s shall have the same customer interface regardless of horsepower rating.

- The VFD keypad shall be backlit and removable to allow uploading and downloading parameter settings.

- The VFD shall be able to communicate via Ethernet without the use of a third-party gateway.

- The keypad shall include hand-off-auto selections with bump less transfer between hand and auto.

- Internal PID functionality shall be supplied with the VFD for closed loop control.

- The VFD shall be able to be programmed via laptop. All interconnecting communications cable, modems, and/or adapters shall be supplied along with a licensed copy of the software.

- Data Display:

  - Output Frequency

  - Motor Current

  - Calculated % Motor Torque Calculated Motor Power (kW) DC Bus Voltage

  - Output Voltage

  - Heatsink Temperature

  - Elapsed Time Meter (reset-able)

  - KWh (resettable)

  - Input / Output Terminal Monitor

  - PID Actual Value (Feedback) & Error Fault Text

  - Warning Text

  - Three (3) Scalable Process Variable Displays

  - User Definable Engineering Units

- Two (2) Programmable Analog Inputs

- Six (6) Programmable Digital Inputs

- Two (2) Programmable Analog Outputs

- Up to Six (6) Programmable Relay Outputs (Three (3) Standard)

- Input Speed Signals”

  - Current O (4) to 20 mA

  - Voltage O (2) to 10 VDC

  - Increase/Decrease Reference Contacts (Floating Point)

  - Serial Communications

- Input Speed Signals:

  - Current O ( 4) to 20 mA

  - Voltage O (2) to 10 VDC

  - Increase/Decrease Reference Contacts (Floating Point)

  - Serial Communications

- Start/Stop:

  - 2 Wire (Dry Contact Closure)

  - 3 Wire (Momentary Contact)

  - Application of Input Power

  - Application of Reference Signal (PID Sleep/Wake-Up)

  - Serial Communications

- Start Functions:

  - Ramp

    - Flying Start

    - Pre-Magnetization (DC Brake) on Start

  - Automatic Torque Boost

  - Automatic Torque Boost with Flying Start

  - Auto Restart (Reset) - Customer Selectable and Adjustable

- Stop Functions:

  - Ramp or Coast Stop

  - Emergency Stop

  - DC Braking / Hold at Stop

  - Flux Braking

- Timer Functions:

  - Four (4) Daily Start/Stop Time Periods

  - Four (4) Weekly Start/Stop Time Periods

  - Four Timers for Collecting Time Periods and Overrides

- Supervision Functions

- Adjustable Current Limit

- Automatic Extended Power Loss Ride Through (Selectable)

- PID Control:

  - Two (2) Integral Independent Programmable PID Setpoint Controllers (Process & External)

  - External Selection between Two (2) Sets of Process PID Controller Parameters

  - PID Sleep/Wake Up

- Motor Control Features:

  - Scalar (V/Hz) and Vector Modes of Motor Control

  - V/Hz Shapes

  - Linear

  - Squared

  - Energy Optimization

  - IR Compensation

  - Slip Compensation

  - Three (3) Critical Frequency Lockout Bands

- Pre-programmable Protection Circuits:

  - Overcurrent

  - Short Circuit

  - Ground Fault

  - Over Voltage

  - Under Voltage

    - Input Phase Loss

  - Output Device (IGBT) Over Temperature

  - Adjustable Current Limit Regulator

  - UL508C approved Electronic Motor Overload (I2T)

- Programmable Fault Functions for Protection Include:

  - Loss of Analog Input

  - Panel Loss

  - External Fault

  - Motor Thermal Protection

  - Stall

  - Under load

  - Motor Phase Loss

  - Ground Fault

- Input Impedance

  - 5% Equivalent Impedance with Internal Reactors(s)

- Include Ethernet Card

  - Modbus/TCP adapter ( one port) shall be included with the specified VFD.

General Specification Requirements:

- Any changes to these features, specifications and requirements shall be put in writing by the vendor and approved by the NELHA Officer-in-Charge (OIC). For the sake of this solicitation and installation of the equipment, the NELHA OIC will be Keith Olson, Chief Operations and Science Officer or his designated representative.

- Manufacturer/Vendor shall provide on-site or on-line (Zoom or Teams) start up assistance by a factory authorized and trained technician.

- Warranty: 2 year on site parts and labor from date of shipment with NELHA Technicians performing the install and start up.

- The VFD shall be ABB ACQ580 Series VFD's for Water Pumping Application, Drive Only; model ABB ACQ580-01-124A-4 or Equal VFD in strict accordance with the above features, specifications, and services.

Communication and Control Requirements:

- New VFD will be required to communicate with, take a lead or following roles in the PID controls with client's current ABB drives. VFD manufacturer shall demonstrate that they can integrate seamlessly with client's current inventory of ABB, ACH 550-UH drives when in PID lead or following roles.

- The VFD should include a Pump and Fan Alteration (PFA) mode of operation. The PFA function should contain the following major features:

  - The VFD controls the motor of pump no. 1, varying the motor speed to control the pump capacity. This motor is the speed regulated motor.

  - Direct line connections power the motor of pump no. 2 and pump no.3, etc. The ACI-1550 switches pump no. 2 (and then pump no. 3, etc.) on and off as needed. These motors are auxiliary motors.

  - The VFD PID control uses two signals: a process reference and an actual value feedback.

  - The PID controller adjusts the speed (frequency) of the first pump such that the actual value follows the process reference.

    - When demand (defined by the process reference) exceeds the first motor's capacity ( user defined as a frequency limit), the PFA control automatically starts an auxiliary pump. The PFA also reduces the speed of the first pump to account for the auxiliary pump's addition to total output. Then, as before, the PID controller adjusts the speed (frequency) of the first pump such that the actual value follows the process reference. If demand continues to increase, PFA adds additional auxiliary pumps, using the same process.

  - When demand drops, such that the first pump speed falls below a minimum limit, the PFA control automatically stops an auxiliary pump. The PFA also increases the speed of the first pump to account for the auxiliary pump’s missing output.

  - An Interlock function (when enabled) identifies off-line (out of service) motors, and the PFA control skips to the next available motor in the sequence.

  - An Auto-change function (when enabled and with the appropriate switchgear) equalizes duty time between the pump motors. Auto-change periodically increments the position of each motor in the rotation - the speed regulated motor becomes the last auxiliary motor, the first auxiliary motor becomes the speed regulated motor, etc.

  - The VFD's programmable relays are capable of interfacing with the PFA function.

- Variable Frequency Drive Modbus Register must contain the following:

  - A Control Word capable of receiving and writing a 16-bit Word from NELHA's current SCADA system for Command/Control purposes.

  - A Reference 1 parameter capable of receiving and writing data from NELHA's current SCADA system with a range of 0 to 20000 for speed control purposes.

  - A Reference 2 parameter capable of receiving and writing data from NELHA's current SCADA system with a range of 0 to 10000 for speed control purposes.

  - A read only STATUS WORD capable writing data to NELHA's current SCADA system for the purpose of monitoring the current status of the VFD.

  - A read only FAULT WORD capable of writing data to NELHA 's current SCADA system for the purposing of monitoring active VFD faults.

Hot Swappable Requirements:

- New VFD will be required to fit in the current VFD wall mounted locations with minimal movement of:

  - Pump motor conductors

  - Communication cables

  - Wall mounted plates and mounting brackets.