SPECIFICATIONS

The State of Hawaii, Department of Human Services, Office of Youth Services, Hawaii Youth Correctional Facility owns and operates motor generators at various sites around the facility.  These motor generators provide backup electrical power in case of commercial power failure.  The motor generators, automatic load transfer switches, and fuel supply systems must be ready to always function to provide for the continuous operation of the emergency and operations equipment located at these sites.  Presently facility maintenance personnel provide monthly exercising of generators, general maintenance, and fueling as needed.

SCOPE

This service shall consist of thorough quarterly maintenance work and inspection in accordance with the best commercial practice governing the maintenance of emergency motor generators.  All labor (including personnel travel costs and per diem), taxes, parts, materials, supplies, consumables (such as, but not limited to, filters, lubricants, and coolant), belts, radiator hoses, tools, equipment, safety gear, costs for storage, transportation, shipping, and supervision as required to accomplish the maintenance activities described herein shall be included in the bid price submitted.

Maintenance activities include responsibility for motor generators, load transfer switches, and fuel supply systems and include the following:

- Routine inspection of generators, transfer switches, and fuel system.

- Routine and pro-active maintenance and repair of generators and transfer switches.

- Fuel replenishment through coordinated efforts with facility maintenance personnel.

- Written documentation of inspection, maintenance, and repair activities.

- Rapid response to emergency requests for maintenance and/or repair (billable extra work).

Maintenance, repair work, and/or fuel replenishment necessary to ensure the continuing availability and operation of the motor generators and related systems will be accomplished as soon as possible.  Required Contractor response times are described herein under “Emergency Response Requirements.”  When possible, the State will work with the Contractor to permit maintenance, repair, or refueling operations that do not impact system availability to be resolved at the Contractor’s next regularly scheduled inspection/maintenance visit.

The Contractor is not responsible for the following:

- Repairs due to flagrant vandalism, fire, storm, or related damages which can be attributed to causes beyond their control.  (However, the Contractor shall be responsible for such repairs if the damages are caused by the Contractor’s failure to properly maintain and service the systems and equipment.)

- Repair or replacement of fuel system components other than furl filters, water traps, and required chemicals.

- Cost of fuel and required fuel additives.

The Contractor is also not responsible unless otherwise specified in these specifications, for any one-time repair costs where the cost of labor, parts, and materials only for the one-time repair event exceeds $250.00 (a “Repair”).  If a Repair is necessary, the contractor will submit a quote for the total cost of the Repair to the State the Contractor must receive approval from the Facility Representative prior to proceeding with the Repair.  Costs for any Repair work performed without the prior approval of the State shall be assumed in full by the Contractor.

DESCRIPTION OF WORK

This service shall consist of thorough maintenance work and inspection in accordance with the best commercial practice governing the maintenance of emergency motor generators.  All labor (including personnel travel costs and per diem), taxes, parts, materials, supplies, consumables (such as, but not limited to filters, lubricants, and coolant), belts, radiator hoses, tools, equipment, safety gear, costs for storage, transportation, shipping, and supervision as required to accomplish the maintenance activities described herein shall be included in the Bid price.

All inspection and maintenance tasks, described herein, shall be performed the same week of the month during operating hours, between the hours of 7:45 a.m. to 4:30 p.m., Monday through Friday, excluding State Holidays, or as otherwise approved in advance by the State.  Any anticipated power outages (regardless of duration), due to maintenance tasks, shall be scheduled with the Facility Operation Section.

The State reserves the right to have maintenance or repair tasks performed on the weekends or after normal operating hours.  Whenever the State exercises this right, the State will compensate the Contractor, for the non-operating hours work, only for one half (1/2) the hourly rate provided by the bidder for its employees, which includes applicable fringe benefit mileage, trave, and tax costs.

QUARTERLY INSPECTION AND MAINTENANCE SERVICES SHALL INCLUDE BUT NOT BE LIMITED TO THE FOLLOWING:

- Check for fuel, oil, and coolant leaks.  Adjust or repair as necessary.

- Check coolant, battery electrolyte and oil levels.  Fill as required.

- Check block coolant heater.  Verify operating properly.

- Inspect cooling system hoses.  Replace if necessary.

- Check air filter.  Clean or replace as necessary.

- Check air intakes, air outlets, and exhaust system for proper operation.  Adjust or repair as necessary.  Report any obstructions or partial blockages.

- Check belts for proper tension and wear.  Adjust or replace as necessary.

- Check engine heater for proper operation.  Adjust or repair as necessary.

- Check transfer tank for proper operation.  Adjust or repair as necessary.

- Check batter electrolyte levels and specific gravity.  Measure and record specific gravity of generator battery.  Fill electrolyte as required.

- Start engine and check emergency system operation with and without load transfer.  Adjust or repair as necessary.

- Inspect silencer.  Adjust or repair as necessary.

- Check generator battery charger operation and verify charge rate is acceptable.  Record charge rate.  Adjust or repair if necessary.

- Check gauges and indicators for proper operation.  Adjust or replace as necessary.

- Check governor speed and adjust for correct frequency at full load.

- Check operation of transfer switch and accessories (such as, but not limited to, programmed delay units) for both utility-to-genset and genset-to-utility transfers.  Ensure that relays and contacts are in working condition, replace as necessary.

- Check engine alternator charge rate.  Adjust or repair as necessary.

- Check generator set controller operation including shutdown functions and emergency stop.

- Check and record generator output voltage under load and adjust as necessary.

- Change oil and oil filter after every 200 hours of operations or and necessary.

- Measure and record fuel levels in main, and if applicable, day tanks.  Replenish diesel fuel as detailed herein.

- Ensure that the areas around the motor generator, transfer switch, and in-building fuel systems are free from debris and other discarded or stored materials,

- Notify the State immediately of any problems or other improper conditions, including safety hazards with either the equipment or the facility so that possible corrective action can be performed or coordinated while maintenance personnel are still at the site.

DIESEL FUEL REPLENISHMENT

The Contractor shall ensure that the main tank fuel level is kept at or above the 75% level.

If fuel is required, the contractor shall notify the Facility Operations of the low fuel situation.  Hawaii Youth Correctional Facility will be responsible to provide fuel as required.

EQUIPMENT VERIFICATION

The Contractor shall submit, within the quarter, the following items:

- Certification that the List of Equipment information has been verified and is correct, or the correct information.

- Fuel tan sizes for each of the generators and the estimated runtime of a full tank.

LIST OF EQUIPMENT

Work specified herein shall apply the following equipment:

SECURE CUSTODY FACILITY BLDG. #1

CATERPILLAR GENERATOR		Model:CAT3406,300K W GENSET
							Engine S/N 4GR02196
							Generator S/N 8KF00886

CATERPILLAR transfer switch		Model:TCF3B6PXF2X3XXXXXX0
							Serial No. 24595

LIFT STATION

GENERAC 20KW				Model:SD020NA
							Serial No. 3016229689

GENERAC transfer switch			Model:00A00165
							Serial No.25651

INSPECTION/MAINTENANCE SERVICE CHECKLIST

Contractor shall prepare and maintain an inspection/maintenance service checklist (See Check List attached) which shall include the inspection/maintenance service.  This checklist must be submitted to the State with the quarterly invoice.  Payment will not be made without valid checklists submittals.

EXAMINATION OF SERVICE AREAS AND EQUIPMENT

Prospective bidders should visit each site to inspect the equipment listed herein; familiarize themselves with the existing conditions; and understand the amount and type of work to be performed.  No additional compensation will be made by reason of any misunderstanding or error regarding compensation will be made by reason of any misunderstanding or error regarding conditions at the service areas or the amount and type of work to be performed. Bidder shall consider the existing equipment to be in “as is” condition. Prospective bidders are responsible for their traveling expenses incurred for the examination of the emergency motor generator equipment.

SITE ACCESS AND SECURITY

Contractor agrees to follow the site access and security procedures of each facility.  Contractor agrees to provide personal background information for its employees as required.

TOOLS, EQUIPMENT AND SUPPLIEIS

Contractor shall provide all tools, equipment, and supplies.  Storage of any tools and supplies at any State facility shall not be allowed without the prior written consent from the State.  Tools and or supplies stored at any State facility without the prior written consent from the State shall be considered abandoned and may be disposed of by the State without compensation to the Contractor.

SAFETY

Contractor must adhere to all Operational Safety and Health Administration (OSHA) regulations.  Contractor must inform employees of electrical hazards when working at a State facility.  Contractor must obey signs and posted notices.

Use or consumption of alcoholic beverages or illegal drugs is not permitted in State facilities.  Smoking is prohibited in the facilities and when handling fuel and or otherwise working with fuel systems.

EMERGENCY CALL-OUT RESPONSE REQUIREMENTS

The Contractor shall provide emergency maintenance, repair and fueling services on an on-call basis for the duration of this contract at the extra work rate described on Page (1 and 2) of bid.  The Contractor shall provide a 24-hour contact number (answering service or voice mail) and will acknowledge requests for emergency services within one (2) hour from the time of the initial request by direct call, call to answering service or call to voice mail.  Emergency maintenance and repair response shall commence within two (2) hours of initial notification.

If the Contractor cannot meet any of the requirements of the Contract, the Contractor shall notify the State immediately by phone and in writing so other arrangements can be made.

Emergency refueling services will be accomplished within twenty-four (24) hours of initial notification.

ALLOWABLE COSTS FOR PARTS

If replacement parts or materials are required for “changeable” emergency services of authorized extra work, the State shall compensate the Contractor for the part(s) at the Contractors cost plus labor (Part C).  The Contractor’s material cost mark-up shall not exceed 20% which shall include shipping, overhead, profit, taxes, and taxes, and any other incidental expenses.  The Contractor shall substantiate all costs by submitting a copy of part or material invoices with their invoice to the State.  Use only new, standard parts or material as manufactured by the maker of each unit or part of equal quality.

EMERGENCY MOTOR GENERATOR CHECKLIST
State of Hawaii, Department of Human Services
Office of Youth Services
Hawaii Youth Correctional Facility

Site Name:			Vendor or Agency:		Service Technician (Print Name):

Date:	Time IN:  Time OUT:		Engine		Engine		Transfer	Main Tank:
					Hours-Start	Hours-End	Fuel Level	Fuel Level

PRESTART CHECKS

_____	Check fuel, oil, coolant levels, condition and for leaks.  Refill or replace as necessary.

_____	Ensure that fuel level is at 75% or higher.  Forward fueling invoice to ICSD representative.

_____	Check battery connection, specific gravity, and water level.  Check charger operation.

Specific Gravity __________	Fluid Qty. Added __________

Float Rate __________  Float Voltage (normal) __________ (cranking) __________

_____	Check governor linkage, oil level and adjust speed according to frequency.

_____	Check cooling system hoses.		__________ Check air filter, intakes, and outlets.

_____ Check belts foe proper tension and wear.	__________ Check engine heater operation.

_____ Check transfer tank for proper operation.	__________ Check gauges and indicators.

OPERATIONAL CHECKS

_____ Check transfer switch and accessary operation.  Ensure contacts are in good repair.

Generator Test Method: _____ Stand-alone; _____  Transfer Switch; _____  Main Circuit Breaker.

Generator: No Loud Volts: _____; Freq. _____; W/Load Volts _____; Freq.  _____; Amps _____

Alternator Charge Rate: Amps_____ at Volts_____. Engine Temp: Preheat_____; Hot______

Oil Pressure: Cold________Hot_______. Exhaust smoke after 5 Minutes: _________

______Ensure that works area is clean and orderly.  Do not store tools or supplies.

Notify Facility Operations Section immediately if any major problems.

Maintenance Supervisor Office: (808) 266-9530	Cellular: (808) 497-0754

Facility Operations Supervisor: Cellular: (808) 799-6944

Note discrepancies found and corrections made if any.

_____________________________________________________________________________

_____________________________________________________________________________

______________________________________________________________________________

Comments: ____________________________________________________________________

Please for via FAX to HYCF Maintenance: (808) 266-9533

SPECIAL PROVISIONS

Term of Contract

The Contractor shall provide quarterly maintenance service for five years provided work performance is satisfactory after review of the Facility Operations Supervisor.  Contractor shall provide emergency and approved extra work for the entire contract period.

Invoicing

The Contractor may submit quarterly invoices for payment, after completing services, for the specified bid amount.  The Contractor shall submit original and two (2) copies of the invoice along with payroll affidavits to:

State of Hawaii
	Department of Human Services
	Hawaii Youth Correctional Facility, Building #1
	42-470 Kalanianaole Hwy.
	Kailua, Hawaii    96734

Attn:  Facility Operations

Bidder Qualifications (The State reserves the right to disqualify any bidder who does not meet these qualifications,)

Experience

The bidder shall have a minimum of three (3) consecutive years of experience (immediately prior to the bid opening date), in the field of motor generator equipment maintenance and repair and complete information on the appropriate offer form page.  The bidder shall provide written documentation to support and verify this experience requirement within three (3) working days of State’s request.  The State reserves the right to be the sole judge of the acceptability and its decision shall be final.

Personnel Qualifications

All personnel servicing the motor generator equipment shall have a minimum of one (1) year of experience in the field of motor generator equipment repair and complete information on the appropriate offer form page.  Upon request by the State, the bidder shall submit written documentation listing all personnel that will be assigned to each site along with work experience and any other documents that support and/or verify work experience.  Bidder shall furnish this information within three (3) working days of State’s request.  The State reserves the right to be the sole judge of the acceptability and its decision shall be final.

Spare Parts

Contractor shall maintain spare parts and materials that are required for normal repairs and maintenance of motor generator equipment.

Examination of Service Areas and Equipment:

Prospective bidders should visit each site to inspect the equipment listed herein; familiarize themselves with the existing conditions; and understand the amount and type of work to be performed.  No additional compensation will be made by reason of any misunderstanding or error regarding conditions at the service areas or the amount and type of work to be performed.  Bidder shall consider the exiting equipment to be in “as is” condition.  Prospective bidders are responsible for their traveling expenses incurred for the examination of the emergency motor generator equipment.  Bidders may contact the Operations Administrator, to arrange for a visit of the facilities to inspect the emergency motor generator equipment.

Submission of bid shall be evidence that the bidder has familiarized themselves with the various equipment and site locations; understands and shall comply with the specifications if a awarded the contract.

No additional compensation shall be made because of any misunderstanding regarding the conditions at the sites, or the amount and type of work to be performed.