	JOSH GREEN, M.D.

GOVERNOR OF HAWAIʻI
KE KIAʻĀINA O KA MOKUʻĀINA ʻO HAWAIʻI


	[image: image3.wmf] 


	KENNETH S. FINK, MD, MGA, MPH

DIRECTOR OF HEALTH

KA LUNA HOʻOKELE



	
	[image: image4.wmf] 

STATE OF HAWAIʻI

DEPARTMENT OF HEALTH

KA ʻOIHANA OLAKINO

P. O. BOX 3378

HONOLULU, HI  96801-3378


	


May 13, 2026
The Department of Health, State Laboratories Division (SLD) is requesting a price quotation to replace Exhaust fan #14 at the State Laboratories Division.
I.  SCOPE OF WORK

Work site is located on the first floor of the State Laboratories Facility located at 2725 Waimano Home Road, Pearl City, HI 96782.
Exhaust fan #14

a. Please see attachments for available information and pictures of the current fan.
b. Contractor shall disconnect exhaust fan #14 from power and controls.

c. Contractor shall remove fan and ducting up to the wall penetration.

d. Contractor shall dispose of ducting, supports, fan, and any other materials that need to be removed for installation of the new fan.

e. Contractor shall order and deliver a new equivalent fan (20000 cfm, .50 static, 544 rpm, 7.5 hp, electrical requirements 460/3/60 see attachment for any other requirements) and other materials to SLD.

f. Contractor shall install new fan with new supports, spring isolation, and connect to the wall penetration with ducting similar to the existing duct work.

g. New Equipment to be coated with PSX‑700 or equivalent high‑performance coating suitable for corrosive/industrial environment, subject to STATE approval.
h. Reconnect the new fan to controls and power.

i. Start up and  Test new fan.  Contractor shall verify correct rotation, airflow, vibration, noise, and control operation in the presence of STATE representative.
General
a. Contractor shall provide shop drawing or manufacture’s installation information no less than 4 weeks prior to the installation of the new equipment.

b. Contractor shall be responsible for delivery of the fan and any other materials required to complete the work.  Contractor shall provide an estimated delivery date for equipment as soon as it is available.
c. All work shall be completed within six (6) months of the notice to proceed, unless otherwise approved by the STATE in writing.

d. Contractor shall be responsible for any fees, taxes, permits, or any other costs associated with the work and should include all such costs as part of their bid price.
e. Contractor shall provide all needed equipment and tools to safely complete the work.
f. All materials purchased for this project shall be new and of current manufacture.

g. Fan shall have a Manufacturer's Warranty which at a minimum provides the following:  One (1) year warranty on parts from date of installation and acceptance to the original user of the equipment if it should prove defective workmanship or defective materials.  The manufacturer shall replace the defective parts without charge to the Government.
h. At completion of the work, Contractor shall provide a written warranty that the completed project is free from any workmanship or material defects for a period of one (1) year months starting from the date of the works formal acceptance.  The warranty shall state that, in case of any workmanship defects that will occur within the period of one (1) year, the Contractor shall implement the necessary corrective work without charging the Government for the costs of materials, labor, and equipment use.
i. All work must be done in accordance with all Federal, State, and Local laws including but not limited to Chapter 104, HRS (State of Hawaii prevailing wage laws).  Contractor’s must be licensed to provide services in the State of Hawaii only used licensed individuals where applicable.
j. All work shall be completed during normal working hours 7:30 am HST– 4:30 pm HST Monday through Friday excluding STATE holidays.  While the STATE may allow for work outside normal hours at the CONTRACTOR’s request, the STATE shall not be responsible for any additional costs associated with after hours or weekend work.  Any such after‑hours work must be pre‑approved in writing by the STATE.
k. Contractor shall dispose of all wastes generated in accordance with all Federal, State, and Local laws and leave the work areas clean.
2. CONTACT
While not required, you may inspect the work site prior to submitting a bid.  Site visits may be scheduled on May 18 @ Noon – 4 pm HST or May 20 @ 8 am – Noon HST.  Not attending a site visit does not relieve the Contractor of the responsibility of understanding the work site conditions prior to placing a bid.  If you have any questions, wish to request additional information, or would like to schedule a site visit, please contact Mr. Stephen Schanzenbach, at 453-6651, fax. 453-6662 or e-mail: stephen.schanzenbach@doh.hawaii.gov.  
3. BID SUBMISSION

Please submit your bid on HIePRO by 2PM HST on May 28, 2026.  Bids submitted outside of HIePRO or after the deadline will not be considered.
4. BASIS OF AWARD
Award shall be made to the lowest responsive, responsible bidder.  STATE reserves the right to reject any or all bids in the STATE’s best interest.
5. PROTESTS
Are allowed for any phase of solicitation and award.

Protest of any phase of solicitation: shall be submitted in writing prior to receipt of offers. (HAR Section 3-126-3)

Protest of an award: shall be submitted in writing within 5 working days of posting of award. (HAR Section 3-126-4)

Stay of Procurement: Once filed, no further action shall be taken on the procurement until the protest has been settled. (HAR Section 3-126-5)

6.  INSURANCE REQUIREMENTS
Vendor must be properly insured and provide a Certificate of Insurance (COI) that covers the service period prior to the start of work. Failure to provide the COI may result in cancellation of the award.  Please see COI attachment for required insurance amounts and details.
7.  TERMS AND CONDITIONS

Please see the attached State of Hawaii General Terms and Conditions.  No modifications to the terms and conditions are allowed.
8.  OTHER INFORMATION

The Hawai‘i Department of Health does not discriminate on the basis of race, color, sex, national origin, age, or disability, or any other class as protected under applicable federal or state law, in administration of its programs, or activities, and, the Department of Health does not intimidate or retaliate against any individual or group because they have exercised their rights to participate in actions protected, or oppose action prohibited, by 40 C.F.R. Parts 5 and 7, or for the purpose of interfering with such rights.

If you have any questions about this notice or any of the Department’s non-discrimination programs, policies, or procedures, you may contact: 


Valerie Kato


Acting Non-Discrimination Coordinator 


Hawai‘i Department of Health 


1250 Punchbowl Street, HI 96813, 


(808) 586-4400 


doh.nondiscrimination@doh.hawaii.gov 

If you believe that you have been discriminated against with respect to a Department of Health program or activity, you may contact the Non-Discrimination Coordinator identified above. 

To request language or accessibility for this document, please contact: the HDOH Non-Discrimination Coordinator, located at 1250 Punchbowl Street, Honolulu, HI 96813 (Phone: (808) 586-4400 or email: doh.nondiscrimination@doh.hawaii.gov). 
Please allow sufficient time for HDOH to meet accommodation requests.

[image: image1.jpg]it RN SN RSy




Exhaust fan #14

[image: image2.jpg]J ..,,\.mmﬁmw'ﬁm@m .

St





Exhaust fan 14 and ductwork.
� EMBED Word.Picture.8  ���





In reply, please refer to:


File:











_1031661413.doc
[image: image1.png]% A~ XS
®0, @
@% © oc®

o2
DL s
©00000000
@"@OB@E\] o
22

(
A/
l’ 2
A







