HALAWA CORRECTIONAL FACILITY (HCF)

ANNUAL FIRE PROTECTION EQUIPMENT INSPECTION AND SERVICING

PERIOD:  MARCH 1, 2019 to FEBRUARY 29, 2020

AMOUNT                                                         DESCRIPTION

295 Each	Fire Extinguishers, Dry Chemical, ABC, 10 lbs.

ANNUAL MAINTENANCE - Visual and physical inspection of cylinders; weight (heft), tag and seal cylinders; certify with tags and provide written reports.

7 Each	Fire Extinguishers, Carbon Dioxide, CO2, 10 lbs.

ANNUAL MAINTENANCE - Visual and physical inspection of cylinders; weight (heft), tag and seal cylinders; certify with tags and provide written reports.  HYDROSTATIC TESTING – Inspection, servicing and testing of cylinders; weight (heft), tag and seal cylinders; certify with tags and provide written reports.

21 Each	Automatic Sprinkler Risers (Wet) and Fire Department Connections

ANNUAL MAINTENANCE - Inspection, servicing and testing of valves and associated parts to ensure proper operation and assurance of good condition; activate tamper switches to send and receive signal at panel; flow from inspector’s test valve to examine alarm bell response; visual check of sprinkler piping; walk through entire location to visually inspect heads and ensure proper coverage; air pressure test Fire Department connections; open main drain and record residual pressure; certify with tags and provide written reports.

8 Each	Fire Hydrants

ANNUAL MAINTENANCE - Inspection, servicing and testing of hydrants, two at a time to ensure proper operation and assurance of good condition; open each hydrant unit to ensure all foreign material has been cleared, record consumption rate, pivot reading, static and residual GPM readings; certify with tags and provide written reports.

4 Each	Dry Stand Pipes and Fire Department Connections

ANNUAL MAINTENANCE – Visual and physical inspection of dry stand pipes; test for sway bracing, hangers and corrosion to ensure that the system is in proper working condition; perform pressure test, air tests, hydrostatic tests, flow tests, gauge tests, onsite water supply test, air pressure test; validate Fire Department connections; certify with tags and provide written reports.

35 Each	Fire Hoses and Fire Department Connections

ANNUAL MAINTENANCE – Inspection, servicing and testing of valves and associated parts to ensure proper operation and assurance of good condition; validate Fire Department connections; certify with tags and provide written reports.

Note:  Installed, certified and tagged February 2016 by National Fire Protection

BID CLOSES:  WEDNESDAY, FEBRUARY 20, 2019 @ 2:00 P.M.

All bids including attachments must be posted on HIePRO by the deadline.

No faxes, telephone, email or hand delivered bids will be accepted.

Contact Person:  Carrick A. Agbayani, General Construction & Maintenance Supervisor, (808) 485-5205